## ModelRun
model_run | TM52? | TM59? | TM59 (Mech Vent)? | description | filtered_runs_to_graph | counter | date | general reference | dewg reference | london_plan_ref | average glazing ratio | U-Value (walls) (w/m2.k) | U-Value (floor) (w/m2.k) | U-Value (roof) (w/m2.k) | U-Value (opaque doors) (w/m2.k) | U-Value (acoustic louvres) (w/m2.k) | G-value | window frame factor | U-Value (windows) (w/m2.k) | door frame factor | Air Permeability (m3/h.m2 @50Pa) | Thermal mass | Ventilation Description | Openable Area: bedrooms | Opening Operational Profile: bedrooms | Openable Area: living room/kitchen | Opening Operational Profile: living room/kitchen | Background Mechanical? | MVHR system heat recovery? | gains description | gains technical params | Cooling description | Cooling Technical Characteristics | Heating description | Heating Technical Characteristics | Adjacent buildings included? | Trees included?
001_Holmsdale_blkA_TM59Overheating | No | No | No | 2300x600mm acoustic ventilation panel for each bedroom and living room, openable day and night, on all facades. All other windows closed | 1 | 0 | 2020-05-11 | Re: J6604 TM59 overheating analysis | J:\J6604\Calcs\IesFolder\TM59_DomesticOverheatingAssessment\02_CAD\20190628 | CIBSE TM59: 2017 | 25% | 0.14 | 0.11 | 0.11 | 2.2 | 0.8 | 0.4 | 0.9 | 1.2 | 1 | 3 | lightweight | Vent via acoustic louvres only. considered open when Ta>22 C. MVHR with summer bypass. a) supply to bedrooms, living room b) extract from toilets and kitchen. | louvres: 50% Free area throughout | TM59_Temp22-Daytime_Temp22-Nighttime <br> | louvres: 50% Free area throughout | TM59_Temp22-Daytime_Temp22-Nighttime <br> | no | yes | as per TM59 | N/A | no cooling |  | UFH | no | yes | no